Document Title

Product Requirements Specification (PRS)

Project: Smart Industrial Temperature Monitoring System

Version: 1.0

Department: Research & Development

Owner: Systems Engineering Team

Status: Approved

1. Purpose

The purpose of this document is to define the functional and technical requirements for the Smart Industrial Temperature Monitoring System (SITMS). The system continuously monitors equipment temperatures in manufacturing environments, detects abnormal conditions, and generates alerts to prevent equipment failures.

2. Business Objectives

- Reduce equipment downtime by 30%.

- Improve predictive maintenance capabilities.

- Increase monitoring accuracy to ±0.5°C.

- Enable real-time dashboard visualization.

- Integrate with existing Manufacturing Execution Systems (MES).

3. Scope

The system shall include:

- Wireless temperature sensors

- Edge gateway

- Cloud-based analytics platform

- Web dashboard

- Mobile notifications

- Historical data storage

- Alert management system

Out of Scope:

- Machine control automation

- PLC programming

- ERP integration

- Billing systems

4. Functional Requirements

| ID | Requirement | Priority |
| --- | --- | --- |
| FR-001 | Collect temperature every 5 seconds | High |
| FR-002 | Store readings in cloud database | High |
| FR-003 | Detect abnormal temperature spikes | High |
| FR-004 | Send email alerts | High |
| FR-005 | Send mobile push notifications | Medium |
| FR-006 | Display live dashboard | High |
| FR-007 | Export historical reports | Medium |
| FR-008 | Generate weekly analytics | Medium |
| FR-009 | Role-based user access | High |
| FR-010 | Support firmware updates | Low |

5. Non-Functional Requirements

Performance

- Support 10,000 sensors simultaneously.

- Dashboard response time under 2 seconds.

- Alert generation within 10 seconds.

- Database query response under 5 seconds.

Availability

- System uptime: 99.9%

- Automatic failover

- Daily backups

Security

- OAuth 2.0 authentication

- TLS 1.3 encryption

- AES-256 encrypted storage

- Role-Based Access Control (RBAC)

Scalability

- Support up to 100 manufacturing plants.

- Horizontal cloud scaling.

- Multi-region deployment.

6. Hardware Requirements

| Component | Specification |
| --- | --- |
| Temperature Sensor | PT100 RTD |
| Accuracy | ±0.5°C |
| Operating Range | -40°C to 250°C |
| Gateway CPU | Quad-core ARM |
| RAM | 4 GB |
| Storage | 64 GB SSD |
| Connectivity | Wi-Fi, Ethernet, LTE |

7. Software Requirements

- Linux Operating System

- Docker Runtime

- MQTT Broker

- PostgreSQL

- REST APIs

- Python Analytics Engine

- React Dashboard

- Kubernetes Deployment

8. Material Requirements

| Material | Reason |
| --- | --- |
| Stainless Steel 316 | Corrosion resistance |
| Aluminum Alloy 6061 | Lightweight housing |
| Silicone Rubber | Waterproof sealing |
| Polycarbonate | Impact-resistant enclosure |

9. Environmental Requirements

| Parameter | Value |
| --- | --- |
| Operating Temperature | -20°C to 70°C |
| Storage Temperature | -40°C to 85°C |
| Humidity | 5–95% RH |
| IP Rating | IP67 |
| Shock Resistance | 20 g |
| Vibration | IEC 60068 compliant |

10. Design Constraints

- Total device weight below 2 kg.

- Manufacturing cost below USD 350 per unit.

- Battery life minimum 24 hours.

- Sensor calibration every 12 months.

- Must comply with IEC safety standards.

11. Assumptions

- Internet connectivity is available.

- Factory power supply is stable.

- Operators have basic technical training.

- Existing network infrastructure supports Ethernet.

12. Risks

| Risk | Impact | Mitigation |
| --- | --- | --- |
| Sensor failure | High | Redundant sensors |
| Network outage | Medium | Local data buffering |
| Battery degradation | Medium | Preventive maintenance |
| False alarms | Low | AI-based filtering |

13. Acceptance Criteria

- Sensor accuracy validated within ±0.5°C.

- 24-hour continuous operation without failure.

- Dashboard latency under 2 seconds.

- Successful cloud synchronization.

- Alert delivery within 10 seconds.

- Data export available in CSV and PDF formats.

14. Success Metrics

| KPI | Target |
| --- | --- |
| Equipment Downtime Reduction | 30% |
| Alert Accuracy | 98% |
| System Availability | 99.9% |
| User Satisfaction | >90% |
| Data Collection Success Rate | 99.5% |

15. Revision History

| Version | Date | Description |
| --- | --- | --- |
| 1.0 | 10-Jan-2026 | Initial Product Requirements Specification |